# G34960005 Master Module

Modbus-RTU slave interface unit

Dupline G34960005: Modbus-RTU slave interface unit.

Interface to Modbus-RTU masters.

Message Descriptions.

The following explains the format and fields for ”03” and ”16” RTU message.

Message (03): Read registers.

Setup (Example):

Master Module:

ID 7 (Dipswitch 1-4: 0111)

128 Dupline channels (Dipswith 5: 0)

PLC:

Start register: 0. (Has always to be one less than the number of the first register)

Number of registers: 5 ( = Dupline A1 to J8).

Send from PLC to Master module:

Byte #:

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- |

| 07 | 03 | 00 | 00 | 00 | 05 | 85 | AF |
| --- | --- | --- | --- | --- | --- | --- | --- |

Byte #1: 	ID number of Master module.

Byte #2: 	Function #. Message ”03” = Read registers.

Byte #3 & 4: 	Starting register.

Byte #5 & 6: 	Number of registers.

Byte #7 & 8: 	Check sum.

Master module to PLC:

Byte #:

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| 07 | 03 | 0A | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | ED |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Byte #1: 	ID number of Master module.

Byte #2: 	Function #. Message ”03” = Read registers.

Byte #3: 	Byte count in Data (Sending 5 registers = 10 bytes = 0Ahex.).

Reg. #1:	Byte #4: 	Data from Dupline b8 – b1.

Byte #5: 	Data from Dupline a8 – a1.

Reg. #2:	Byte #6: 	Data from Dupline d8 – d1.

Byte #7: 	Data from Dupline c8 – c1.

Reg. #3:	Byte #8: 	Data from Dupline f8 – f1.

Byte #9: 	Data from Dupline e8 – e1.

Reg. #4:	Byte #10: 	Data from Dupline h8 – h1.

Byte #11: 	Data from Dupline g8 – g1.

Reg. #5:	Byte #12: 	Data from Dupline j8 – j1.

Byte #13: 	Data from Dupline i8 – i1.

Byte #14 & 15:	Check sum.

Example: Read Digital signals: a7, g3 and j8 ON.

Send from PLC to Master module:

Byte #:

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- |

| 07 | 03 | 00 | 00 | 00 | 05 | 85 | AF |
| --- | --- | --- | --- | --- | --- | --- | --- |

Byte #1: 	ID number of Master module.

Byte #2: 	Function #. Message ”03” = Read registers.

Byte #3 & 4: 	Starting register.

Byte #5 & 6: 	Number of registers.

Byte #7 & 8: 	Check sum.

Master module to PLC:

Byte #:

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| 07 | 03 | 0A | 00 | 40 | 00 | 00 | 00 | 00 | 00 | 04 | 80 | 00 | 3C | B2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Byte #1: 	ID number of Master module.

Byte #2: 	Function #. Message ”03” = Read registers.

Byte #3: 	Byte count in Data (Sending 5 registers = 10 bytes = 0Ahex).

Reg. #1:	Byte #4: 	Data from Dupline b8 – b1 (All OFF).

Byte #5: 	Data from Dupline a8 – a1 (40hex = 64dec = 01000000bin = Dupline a7 ON).

Reg. #2:	Byte #6: 	Data from Dupline d8 – d1 (All OFF).

Byte #7: 	Data from Dupline c8 – c1 (All OFF).

Reg. #3:	Byte #8: 	Data from Dupline f8 – f1 (All OFF).

Byte #9: 	Data from Dupline e8 – e1 (All OFF).

Reg. #4:	Byte #10: 	Data from Dupline h8 – h1 (All OFF).

Byte #11: 	Data from Dupline g8 – g1 (04hex = 04dec = 00000100bin = Dupline g3 ON).

Reg. #5:	Byte #12: 	Data from Dupline j8 – j1 (80hex = 128dec = 10000000bin = Dupline j8 ON).

Byte #13: 	Data from Dupline i8 – i1 (All OFF).

Byte #14 & 15:	Check sum.

Example: Read AnaLink signal: a4 (PT1000 Temp. Transmitter).

It is necessary to increase the numbers of registers we wants to read in the PLC. AnaLink value from A1 is placed in register 9.

Remember: It will take aprox. 30 sec. before getting a result.

Send from PLC to Master module:

Byte #:

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- |

| 07 | 03 | 00 | 00 | 00 | 0A | C5 | AB |
| --- | --- | --- | --- | --- | --- | --- | --- |

Byte #1: 	ID number of Master module.

Byte #2: 	Function #. Message ”03” = Read registers.

Byte #3 & 4: 	Starting register.

Byte #5 & 6: 	Number of registers.

Byte #7 & 8: 	Check sum.

Master module to PLC:

Byte #:

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| 07 | 03 | 14 | 00 | 08 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 99 | 00 | 80 | DC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Byte #1: 	ID number of Master module.

Byte #2: 	Function #. Message ”03” = Read registers.

Byte #3: 	Byte count in Data (Sending 10 registers = 20 bytes = 14hex.).

Reg. #1:	Byte #4: 	Data from Dupline b8 – b1 (All OFF).

Byte #5: 	Data from Dupline a8 – a1 (08hex = 08dec = 00001000bin = Dupline a4 ON).

Reg#2-8	Byte #6-#19: 	Data from Dupline p8 – p1 (All OFF).

Reg. #9:	Byte #20: 	Data from Dupline AnaLink A2 (OFF).

Byte #21: 	Data from Dupline AnaLink A1 (OFF).

Reg #10:Byte #22: 	Data from Dupline AnaLink A4 (99hex = 153dec = 24(C).

Byte #23: 	Data from Dupline AnaLink A3 (OFF).

Message (16): Write registers.

Setup (Example):

Master Module:

ID 7 (Dipswitch 1-4: 0111)

128 Dupline channels (Dipswith 5: 0)

PLC:

Start register: 0. (Has always to be one less than the number of the first register)

Number of registers: 5 ( = On Dupline: A1 to J8).

Send from PLC to Master module:

Byte #:

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| 07 | 10 | 00 | 00 | 00 | 05 | 0A | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | E2 | 98 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Byte #1: 	ID number of Master module.

Byte #2: 	Function #. Message ”16” (10 hex  = 16 bin = Write registers).

Byte #3 & 4: 	Starting register.

Byte #5 & 6: 	Number of registers.

Byte #7: 	Byte count (Sending 5 registers = 10 bytes = 0Ahex).

Reg. #1:	Byte #8: 	Data from Dupline b8 – b1.

Byte #9: 	Data from Dupline a8 – a1.

Reg. #2:	Byte #10: 	Data from Dupline d8 – d1.

Byte #11: 	Data from Dupline c8 – c1.

Reg. #3:	Byte #12: 	Data from Dupline f8 – f1.

Byte #13: 	Data from Dupline e8 – e1.

Reg. #4:	Byte #14: 	Data from Dupline h8 – h1.

Byte #15: 	Data from Dupline g8 – g1.

Reg. #5:	Byte #16: 	Data from Dupline j8 – j1.

Byte #17: 	Data from Dupline i8 – i1.

Byte #18 & 19:	Check sum.

Master module to PLC:

Byte #:

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- |

| 07 | 10 | 00 | 00 | 00 | 05 | 00 | 6C |
| --- | --- | --- | --- | --- | --- | --- | --- |

Byte #1: 	ID number of Master module.

Byte #2: 	Function #. Message ”16” (10hex = 16 bin = Write registers).

Byte #3 & #4: 	Starting register.

Byte #5 & #6: 	Number og registers.

Byte #7 & #8: 	Check sum.

Example: Write Digital signals: b2, e7 and i4 ON.

Send from PLC to Master module:

Byte #:

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| 07 | 10 | 00 | 00 | 00 | 05 | 0A | 02 | 00 | 00 | 00 | 00 | 40 | 00 | 00 | 00 | 08 | E2 | 98 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Byte #1: 	ID number of Master module.

Byte #2: 	Function #. Message ”16” (10h = 16 bin = Write registers).

Byte #3 & 4: 	Starting register.

Byte #5 & 6: 	Number of registers.

Byte #7: 	Byte count (Sending 5 registers = 10 bytes = 0A Hex).

Reg. #1:	Byte #8: 	Data from Dupline b8 – b1 (02hex = 02 dec = 00000010 bin = Dupline b2 ON).

Byte #9: 	Data from Dupline a8 – a1 (All OFF).

Reg. #2:	Byte #10: 	Data from Dupline d8 – d1 (All OFF).

Byte #11: 	Data from Dupline c8 – c1 (All OFF).

Reg. #3:	Byte #12: 	Data from Dupline f8 – f1 (All OFF).

Byte #13: 	Data from Dupline e8 – e1 (40 hex = 64 dec = 01000000 bin = Dupline e7 ON).

Reg. #4:	Byte #14: 	Data from Dupline h8 – h1 (All OFF).

Byte #15: 	Data from Dupline g8 – g1 (All OFF).

Reg. #5:	Byte #16: 	Data from Dupline j8 – j1 (All OFF).

Byte #17: 	Data from Dupline i8 – i1 (08 hex = 08 dec = 00001000 bin = Dupline i4 ON).

Byte #18 & 19:	Check sum.

Master module to PLC:

Byte #:

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- |

| 07 | 10 | 00 | 00 | 00 | 05 | 00 | 6C |
| --- | --- | --- | --- | --- | --- | --- | --- |

Byte #1: 	ID number of Master module.

Byte #2: 	Function #. Message ”16” (10 hex = 16 bin = Write registers).

Byte #3 & #4: 	Starting register.

Byte #5 & #6: 	Number og registers.

Byte #7 & #8: 	Check sum.